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725 E. Main Street
Flushing, Michigan 48433
810-659-5665 – telephone
810-659-0569 – facsimile
www.flushingcity.com

MOBILE FOOD SERVICE UNIT PERMIT APPLICATION
AND FIRE/SAFETY INSPECTION FORM

Date: ___________________	Location: ______________________	City Permit #: _____________

Inspecting MI FDID: _______	Inspectors MI CFI#: ______________	Dates/Times: _____________
BUSINESS INFORMATION:
Name: ________________________________________________________________________
Address: ______________________________________________________________________________
		Street/Apt #			City			State			Zip
Phone: _____________________	Email: __________________________________________
Website: ______________________________________________________________________
BUSINESS OWNER INFORMATION:
Last: ____________________________First: _____________________________	MI: ________ 
Address: ______________________________________________________________________
		Street/Apt #			City			State			Zip
Phone: _____________________	Email: __________________________________________
Driver’s License #: _____________________State: ______Exp: ____________ DOB: _________
VEHICLE OPERATOR INFORMATION:
Last: ____________________________First: _____________________________	MI: ________ 
Address: ______________________________________________________________________
		Street/Apt #			City			State			Zip
Phone: _____________________	Email: __________________________________________
Driver’s License #: _____________________State: ______	Exp: ____________ DOB: _________
VEHICLE INFORMATION:
Make: ________________ Model: ________________ Year: __________ Unit #: ____________
Plate #: _______________________ State: ________ Type: ____________Exp: _____________
VIN:__________________________________________________________________________Registrant:_____________________________________________________________________
Insurer: ___________________________Policy #: ____________________Exp: _____________
VEHICLE INFORMATION
	
	LPG (Propane)
	
	CNG (Compressed Natural Gas)

	
	Generator
	
	Solar

	
	Stove
	
	Oven

	
	Deep Fryer
	
	Solid

	
	Hood System
	
	Automatic Fire Suppression



Date: ___________________________	Fee Paid Permit: _____$______________________
Date: ___________________________	Fee Paid Inspection: __$______________________
					 	Total of Fees Paid: ___$______________________

Approved: _____________________________________________________________________	
		Monica M. Zofchak, City Clerk 


	INSPECTION CRITERIA

	OK
	VIOL
	OOS
	N/A
	OK:  COMPLIANT
VIOL: NOT COMPLIANT
OOS: CURRENT CONDITION IS UNSAFE TO OPERATE CREATING AN OUR OF SERVICE CONDITION
N/A: NOT APPLICABLE

	FIRE EXTINGUISHERS

	
	
	
	
	Fire Extinguishers are to be inspected and tagged annually (96:10.9.5)

	
	
	
	
	2A10BC or larger fire extinguisher required on MFSU’s.  Except hand propelled carts that do not have fossil fuel powered equipment (96:10.9.1)

	
	
	
	
	3A40BC or larger fire extinguisher required when equipped w/a portable generator.  The 2A10BC extinguisher is not required to be in addition to the 3A40BC. (96:10.9.1)

	
	
	
	
	A 1.5-gal Class K fire extinguisher is required for solid fuels, cooked vegetable or animal oils and fats (96:10.9.2)

	
	
	
	
	Fire Extinguishers are to be readily accessible. (96:10.9.1)

	ELECTRICAL

	
	
	
	
	Installation Of electrical equipment shall comply with the National Electric Code.  (Spliced Wiring, multi-strops no plugged directly into an outlet, wiring not in conduit)

	SPECIAL HAZARDS

	
	
	
	
	At least one listed carbon monoxide detector is required for all Mobile Food Service Units except open air hand propelled carts (319.9.4 – N1:50.7.11.2)

	
	
	
	
	“No Smoking” sign conspicuously posted inside MFSU (310.2 -N1:10.9.1)

	LPG/CNG/OTHER

	
	
	
	
	At least one flammable gas leak detector is required for Mobile Food Service Units to be installed in the vicinity of fuel burning components in accordance with manufacturers’ instructions (319.6.5)

	
	
	
	
	

	
	
	
	
	Flammable gas leak detection equipment shall be tested at a minimum monthly.  The test to be documented and made available to Fire Code Official upon request.  (1:50.7.2.3.4.3)

	
	
	
	
	MFSU equipped with LPG system, but without current approved LPG certification shall not be permitted to be operated for MFS. Only ASME or DOT/n LPG containers permitted.  (1:50.7.2.3.4.3)

	
	
	
	
	Hydrostatic Test Date:                                                                  Visual Examination Date:

	
	
	
	
	LPG shutoff valves to be readily accessible & Identified by reflective permanent signage.  Letters to be a minimum of 2” high stating “EMERGENCY GAS SHUT OFF VALVE” contrasting to its background. (1:50.7.2.2.3)

	 
	
	
	
	The signage to be weather resistant, clearly visible and unobscured.

	
	
	
	
	The emergency control shut-off to be a quarter turns manual gas ball valve.

	
	
	
	
	The LPG Supply system, including containers shall be installed on the exterior of the vehicle.  Pressure relief valves to be directed in an outward direction away from entry doors.  (58:6.26.3.3)

	
	
	
	
	OR In a vapor tight cabinet not internally accessible.  Accessed from and vented to the outside.  Vented near the top and bottom of the enclosure and 3’ horizontally away from any opening into the vehicle below the level of the vents.  Never stored or transported in the vehicle. (N1:50.7.2.4.3.2.)

	
	
	
	
	LPG Container cannot extend further than the rear bumper and to be protected from vehicle impact.  The bottom of the container shall be mounted higher that 36” from the ground.

	
	
	
	
	LPG container to be secured with a non-combustible material or device.  The container when secured shall not become loose, slip, turn or rotate.

	
	
	
	
	LPG Container to be located in a manner to minimize exposure to excessive temperature rises, physical damage and/or tampering.

	
	
	
	
	Signage stating “No Smoking” with minimum 4” letters contrasting to its background shall be installed above LOG container.

	
	
	
	
	Hose used to pipe LPG to the device must be UL or FM listed and marked for LP use with minimum of 350 psi working pressure.

	
	
	
	
	Couplings, fittings devices and any other appurtenances regarding LPG shall meet UL or FM requirements

	
	
	
	
	Fixed piping shall be designed, installed, supported and secured to minimize damage from vibration, strain, wear, or loosening in transit.

	
	
	
	
	Steel black piping shall have a minimum wall thickness of .049”. (58:6.26.5.1A)

	
	
	
	
	Gas piping shall be installed to enter the vehicle through the floor or wall and travel directly behind to the appliance served.

	
	
	
	
	Branch lines when installed shall have a tee connection located in the main line under the floor and outside the vehicle. 

	
	
	
	
	Exposed fixed piping system shall be corrosion resistant or be coated or protected to minimize corrosion.

	
	
	
	
	A flexible connector shall be installed between the regulator outlet and the fixed piping system to protect against expansion, contraction, jarring and vibration.  (58:6.26.5.1(B))

	
	
	
	
	Flexibility shall be provided in the piping between a cylinder and the gas piping system or regulator.

	
	
	
	
	Regulator vent openings shall be protected from sleet, snow, freezing, rain, ice, mud and wheel spray. 

	
	
	
	
	Maximum aggregate amount of LPG shall not exceed 200 pounds.  (319.8.1)

	
	
	
	
	Any hose being utilized in the fuel line system to be approved.

	
	
	
	
	Fuel piping systems including hose to be pressure tested and proven free of leaks: to be corrosion resistant, coated or protected.

	
	
	
	
	LPG utilized in transit for cargo heater or cooling system shall be designed for in transit use and have a means installed to stop the flow of gas in the event of a line break, such as excess flow valve.

	
	
	
	
	MFSU utilizing Compressed Natural Gas (CNG) shall not exceed an aggregate amount of 1300 pounds. (IFC 319.9.1.1)

	
	
	
	
	CNG containers to be securely mounted and restrained to prevent movement and vehicle impact. (IFC 319.9.1.2)

	
	
	
	
	CNG system piping including valves and fittings shall be adequately protected to prevent tampering, impact damage and damage from vibration. (IFC 319.9.3)

	
	
	
	
	CNG containers expire every three years and shall not be utilized beyond the three years without an inspection by a qualified service facility.  A tag shall be affixed on the CNG System or within the MFSU. (IFC 319.10.3)

	SOLID FUELS

	
	
	
	
	Solid fuel is not stored above any heat producing appliance or vent. (96:14.9.3.2.2)

	
	
	
	
	Solid fuel is not stored closer than 3’ to any cooking appliance. (96:14.9.3.2.2) 

	
	
	
	
	Solid fuel is not stored near any combustible or flammable liquids, ignition sources, chemicals, food supplies, and packaged goods.  (96:14.9.2.7)

	
	
	
	
	Solid fuel ash, cinders, and other fire debris should be removed from the fire box at regular intervals and at least once a day. (96:14.9.3.6.1)

	
	
	
	
	Solid fuel ashes, cinders and other removed fire debris should be placed in a closed, metal container located at least 3’ from any cooking appliance.  (96:14.9.3.8)

	GENERATOR

	
	
	
	
	Refueling of generators to be performed in an approved location not less than 20’ from the MFSU

	
	
	
	
	Generator not to be refueled in areas occupied by the public.

	
	
	
	
	Fuel to be stored in a UL or FM approved flammable liquid metal safety container.

	
	
	
	
	Fuel to be stored in an approved location and secured from movement during transit.

	
	
	
	
	Fuel not to be stored in occupant space of MFSU while generator is in operation.

	
	
	
	
	Generator not to be fueled until both the engine and fuel tank are cool and below the auto ignition temperature of the fuel.  Generator never to be refueled while running.  (1:11.7.2.1.2)

	
	
	
	
	Generator servicing a MFSU shall not be fueled while the Mobile Food Service Unit is in operation.  (1:66.6.5 – IFC 5703.1.1)

	
	
	
	
	Generator to be grounded in an approved method.

	
	
	
	
	Generator while operating shall not exceed 80 decibels at 15 feet.

	
	
	
	
	Generator not to be positioned adjacent to any means of egress, air intakes, openings, building, structure, or vehicle.  (1:11.7.2.2 and BP)

	FIRE PROTECTION INFRASTRUCTURE

	
	
	
	
	MFSU not to be parked in any manner that obstructs a fire lane. (1:50.7.1.7)

	
	
	
	
	MFSU not to be parked in any manner that obstructs a fire hydrant.

	
	
	
	
	MFSU not to be parked in any manner that obscures a fire department connection or other fire protection equipment. (1:50.7.1.7)

	SEPARATION AND SECUREMENT

	
	
	
	
	MFSU not to be within 10’ of entrances/exits of buildings/structures, combustible materials, vehicles, including other MFSU or other cooking operations.  (1:50.7.1.5)

	
	
	
	
	MFSU to be secured from accidental movement by the chocking of the tires.  Chock both sides of tire.  Are wheel chocks present for use? (1:50.7.1.3)

	MEANS OF EGRESS

	
	
	
	
	Clear unobstructed height over the aisle way portion of the unit to be a minimum of 74” from floor to ceiling

	
	
	
	
	A minimum width of 30” of unobstructed aisle space.

	
	
	
	
	A minimum of two means of egress is required if travel distance exceeds 10’ within any portion of the unit.

	
	
	
	
	The location of the secondary means of egress shall be remote from the primary.

	
	
	
	
	Secondary means of egress shall have an unobstructed minimum passage of 24” x 24” to the outside.

	
	
	
	
	The bottom of the secondary means of egress shall not be more than 4’ above the vehicle floor or readily accessible.

	
	
	
	
	The horizontal space in front of the secondary means of egress shall be capable of supporting a minimum weight of 300 pounds at the opening to the outside.

	
	
	
	
	Secondary means of egress shall be labeled “EXIT” with 2” minimum letters on a contrasting background.

	
	
	
	
	The latching mechanism on any exit shall be operable by a single hand with a single motion to open.

	COOKING SYSTEMS – HOOD – AUTOMATIC FIRE SUPPRESSION SYSTEM

	
	
	
	
	Class 1 hood is required if operation involves the cooking of solid fuel, vegetable oil or animal fats.  (IFC 319.3 NFPA 1:50.2.1.1.1/96:4.1.1)

	
	
	
	
	Exhaust hood required if operation releases smoke or steam. (NFPA 96:4.1.1) 

	
	
	
	
	Cooking equipment, hood and exhaust system to be cleaned of grease laden residue with current cleaning certificate/label present. (IFC 607.3.3.3.1/NFPA 96:1.1.6.13)

	
	
	
	
	Fire suppression system to be tagged and certified within the last 6 months.

	
	
	
	
	Hand pull fire suppression system to be unobstructed and in path of egress. 

	
	
	
	
	8” steel baffle required between fryer and surface flames of an adjacent appliance. (96:12.1.2.5)

	
	
	
	
	16” space between fryer and surface flames from adjacent cooking equipment. (96:12.1.2.4)

	
	
	
	
	Cooking Oil Storage shall not exceed a maximum aggregate amount more than 120 gallons on the MFSU (Fc 319.6) 

	
	
	
	
	Deep fat fryers shall have a high-limit control to shut off fuel or energy when the temperature reaches 475 degrees at 1” below the surface.

	
	
	
	
	Positive closing lid required on fryers.  A latching mechanism that secures the lid open or closed.  The lid to be secured closed during transit.



	
	APPROVED
	
	DENIED A re-inspection is required for approval
	Re-Inspection conducted on:  
	A
	D

	
	APPROVED
	
	DENIED A re-inspection is required for approval
	Re-Inspection conducted on:  
	A
	D

	
	YES
	
	NO (Proof of attendance at an approved MFSU Safety Class within the last three years is required to operate)



____________________________ __________  ____________________________ __________ 
Inspector Signature			              Date	           Re-Inspector Signature			      Date
MI/BFS CFI#: _______________________________		           MI/BFS CFI#: ________________________________


____________________________ __________  ____________________________ __________ 
Re-Inspector Signature		              Date	           Re-Inspector Signature			      Date
MI/BFS CFI#: _______________________________		           MI/BFS CFI#: ________________________________
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